EB308R

Installation Instructions for IO Expansion Card

- Product Confirmation

| EB308R board | M3 Screw |
| --- | --- |

- Component Name

| No. | Name | Instructions |
| --- | --- | --- |
| a | Mounting hole | Use M3 screw to install the EB308R board to the inverter |
| b | Terminal | Connect wiring for customer |
| c | Connector | Connect to the inverter |
| d | Plastic handle | Remove EB308 board |

- Electrical Specifications

| Terminal form | Terminal name | Function instructions | Terminal specification |
| --- | --- | --- | --- |
| Relay outputs | A10, C1 | Multi-function relay outputs 8 groups; A-C is the normally open contact. | Maximum voltage: 30VDC or 250VAC Maximum current: Resistive load:5A NO Inductive load: 2A NO (cosΦ=0.4) |
|  | A11, C1 |  |  |
|  | A12, C2 |  |  |
|  | A13, C2 |  |  |
|  | A14, C3 |  |  |
|  | A15, C3 |  |  |
|  | A16, C4 |  |  |
|  | A17, C4 |  |  |

- Wiring Schematic Diagram

- Installation(SA3)

Step1: As the Figure 1 shows, please insert EB308R into the control board SLOT 2 or SLOT 3, not SLOT 1.

Step2: Please lock the two M3 screws with screwdriver according to the torque of 4-6kgf.cm and the direction showed in

Figure 2.

Note: When removing EB308R board, please first remove the right and left M3 screws, and then lift the plastic handle by hand.

Figure 1                                   Figure 2

- Installation (SE3)

Step 1：Turn off the power.

Step 2：Open the top coverof the inverter.

Step 3：Use the front rear as support and slide (a) in by pressing down as figure 1 shown.

Figure 1

Note: (a)-Optional Card Housing; (b)-Hook, (c)-Slot

Step 4: Line up the connector (c) and (d), and press down the EB308R expansion card to the right position.

Figure 2

（a）(e)-Supporter, (b)-Plastic Handle, (c)-Male connector, (d)-Female connector

Step 5: Tighten two M3 screws with 4-6kgf.cm torque on the card. Install the cover after wiring.

Need Cutout this area for installating the cover

Figure 3                             Figure 4

- Others

To improve our products, the parameters and contents may be modified, please contact the agent or refer to Shihlin websites

(http://automation.seec.com.tw/) to download the latest version.