EB362R

Installation Instructions for IO Expansion Card

- Product Confirmation

| EB362R board | M3 Screw |
| --- | --- |

- Component Name

| No. | Name | Instructions |
| --- | --- | --- |
| a | Mounting hole | Use M3 screw to install the EB362R board to the inverter |
| b | Terminal | Connect wiring for customer |
| c | Connector | Connect to the inverter |
| d | Switch | Switch to SINK or SOURCE, and the default state is SINK. |
| e | Plastic handle | Remove EB362 board |

- Electrical Specifications

| Terminal form | Terminal name | Function instructions | Terminal specification |
| --- | --- | --- | --- |
| Switch signal input | M10 | There are totally 6 multifunction expanded control terminals. (Sink/Source can be switched) | Input impedance: 4.7 kΩ Action current: 5mA Voltage range: 10~28VDC Maximum frequency: 1kHz |
|  | M11 |  |  |
|  | M12 |  |  |
|  | M13 |  |  |
|  | M14 |  |  |
|  | M15 |  |  |
| Relay output | A10，C10 | Multi-function relay outputs 2 groups; A-C is the normally open contact | Maximum voltage: 30VDC or 250VAC Maximum current: Resistive load: 5A NO Inductive load: 2A NO (cosΦ=0.4) |
|  | A11，C11 |  |  |
| Public terminal | SD | The common terminal of Terminal M10~M15 (SINK) | --- |
|  | PC | The common terminal of Terminal M10~M15 (SOURCE) | Output voltage: 24VDC±20% Maximum current: 200mA(share with control board) |

- Wiring Schematic Diagram

- Installation(SA3)

Step1: As the Figure 1 shows, please insert EB362R into the control board SLOT 2 or SLOT 3, not SLOT 1.

Step2: Please lock the two M3 screws with screwdriver according to the torque of 4-6kgf.cm and the direction showed in

Figure 2.

Note: When removing EB362R board, please first remove the right and left M3 screws, and then lift the plastic handle by hand.

Figure 1                                   Figure 2

- Installation (SE3)

Step 1：Turn off the power.

Step 2：Open the top coverof the inverter.

Step 3：Use the front rear as support and slide (a) in by pressing down as figure 1 shown.

Figure 1

Note: (a)-Optional Card Housing; (b)-Hook, (c)-Slot

Step 4: Line up the connector (c) and (d), and press down the EB362R expansion card to the right position.

Figure 2

（a）(e)-Supporter, (b)-Plastic Handle, (c)-Male connector, (d)-Female connector

Step 5: Tighten two M3 screws with 4-6kgf.cm torque on the card. Install the cover after wiring.

Need Cutout this area for installating the cover

Figure 3                             Figure 4

- Others

To improve our products, the parameters and contents may be modified, please contact the agent or refer to Shihlin websites

(http://automation.seec.com.tw/) to download the latest version.